## Slide 1: LECTURE 04 COMBUSTION CALCULATIONS (Part B ) ENERGY BALANCE CALCULATIONS Course Outcome Perform and analyse mass and energy balances of a system involving combustion reaction

## Slide 2: GENERAL ENERGY BALANCE
A = any reactant or product
nA = moles of A produced or consumed
vA = stoichiometric coefficient of A
= standard heat of combustion
= enthalpy of reactant / product
Fuel
Air
Reactants Products
Flow rate ?
T oC?
Flow rate ?
T oC?
CO2 ,H2O,
CO, N2 ,O2 ….
Q = DH =?

## Slide 3
Why Perform Combustion Analysis?
ENERGY

## Slide 4: Boiler Heat Losses

## Slide 5: Heat Balance – Sankey Diagram
Heat
Input
Useful
Heat
Sensible Loss
Latent
Loss
Potential + Radiation
+ Convection Losses
Uncounted Losses e.g. opening, conveyor etc
Gross CV Net CV
Assuming the main source of energy/heat input comes only from the fuel and air only acts a source of oxidant unless it is preheated (usually from 25oC) to a specific elevated temperature

## Slide 6: Heat Input
  Energy from fuel :- heating or calorific value (HV or CV ) - Quantity of heat release from combustion of unit weight or volume of fuel (MJ/kg or Kcal/kg or Kcal/ m3 or MJ/m3)
    Higher or gross CV (HCV or HHV) – when liquid water as a combustion product – taking account the presence of water vapor in flue gases
    Lower or net CV (LCV or LHV) – when vapour water as a combustion product - the difference between higher CV and the heat absorbed (latent heat) by water in having its phase changing to vapour
  Energy from air :- usually not counted unless at elevated temperature (preheated air)

## Slide 7: Heating /Calorific Values of Selected Fuels at 25oC and 1 atm

## Slide 8: Heat Losses in Flue Gas
Heat losses in the products of combustion or flue gas can be classified into several types;
  Dry Flue Gas Loss - Heat is lost in the "dry" products of combustion, which carry only sensible heat since no change of state was involved , i.e., the total enthalpy of the various component gases (CO2, N2, O2, SOx , NOx) at the dry flue gas temperature
  Moisture Loss – Heat lost due to combustion of hydrogen (in form of water vapour (sensible heat) or liquid water (latent heat if gross calorific or heating value is considered)
  Potential heat , i.e. the available heat due to the presence of carbon monoxide (CO) and unburned fuel

## Slide 9: Heat Loss Analysis In Flue Gas
Gross CV based heat loss
Net CV based heat loss should exclude the heat condensation of water vapour at 25oC

## Slide 10
Sensible heat in dry flue gas
ni = molar or volumetric flowrate of flue gas component, i…. (CO2, N2, O2, SOx , NOx)
Heat in moisture (vapour)
Potential heat in due to the presence of combustibles in flue gas

## Slide 11: Heat Capacities

## Slide 12
Vapor only

## Slide 13: Water / Steam Properties

## Slide 14: Other Sources of Heat Losses
Loss due to radiation and convection
  This loss occurs from the external surfaces of a combustion equipment
Losses from unaccounted sources such as
  conveyer opening
  incombustibles (ash)
  blowdown
  moisture in air or fuel
  Standby

## Slide 15: Combustion Efficiency
Combustion efficiency is a measurement of how well the fuel is being burned .
The combustion efficiency calculation considers both the flue gas temperature and the net heat and moisture losses.
  This would include losses from dry gas plus losses from the moisture and losses from the unburned fuel as well as the production of CO
Flue gas loss is a measure of the heat carried away by dry flue gases and the moisture loss. It is a good indicator of appliance efficiency.

## Slide 16
The flue gas temperature is the temperature of the combustion gases (dry and water vapor) leaving the appliance, and reflects the energy that did not transfer from the fuel to the heat exchanger.
  The lower the flue gas temperature, the more effective the heat exchanger design or heat transfer and the higher the fuel-to-air/water/steam efficiency is.
  However, if the flue gas temperature is too low (i.e. below the dew point temp), water vapour will be condensed and could cause to a chimney such as downdraft or corrosion.

## Slide 17
Percentage of Combustion efficiency
For maximum combustion efficiency low excess air is desirable
Burners resulting in low levels of unburned fuel & CO while operating at low excess air levels are considered efficient
Well designed burners firing gaseous and liquid fuels operate at excess air levels of 15% and result in negligible unburned fuel - less heat from the combustion process is being used to heat excess air, which increases the available heat for the load.
Combustion efficiency is not the same for all fuels and, generally, gaseous and liquid fuels burn more efficiently than solid fuels

## Slide 21: Thermal Efficiency
Thermal efficiency is a measure of the effectiveness of the heat exchanger of combustion system.
  It measures the ability of the exchanger to transfer heat from the combustion process to process heating medium such as water , steam or air.
  It accounts for the effectiveness of the heat exchanger as well as the radiation and convection losses
  sometimes known as fuel-to-air/water/steam efficiency
What is the maximum theoretical thermal efficiency??

## Slide 22
Example 6
Methane is completely burned with 10% excess air in a boiler. 90 % of the methane burns to form CO2 and the remaining 10% to form CO. Both air and methane enter the boiler at 25oC and the combustion products leaving the boiler is at 300oC.
On the basis of 1 kmol of the methane and the lower fuel heating value, develop a sankey diagram showing the percentage of useful heat and heat losses from various sources with respect to the net calorific value of the fuel.
Heat losses due to radiation, convection and from other uncounted sources is negligible.

## Slide 23
PFD and summary of Mass Balance
Methane
1000 mol/hr
Air
10 % excess air
10476 mol/hr
mol/hr CO2
mol/hr CO
mol/hr H2O
mol/hr O2
mol/hr N2
25 oC
25 oC
300 oC
900
100
2000
250
8276
Q

## Slide 24: Heat Balance – Sankey diagram
Heat
Input
Useful
Heat
Sensible Loss
(N2, O2, CO2)
Latent
Loss (H2O)
Potential (CO) + Radiation
+ Convection Losses
Uncounted Losses e.g. opening, conveyor etc
Gross CV Net CV
Assuming the main source of energy/heat input comes only from the fuel and air only acts a source of oxidant unless it is preheated (usually from 25oC) to a specific elevated temperature

## Slide 25: Heating /Calorific Values of Selected Fuels at 25oC and 1 atm

## Slide 26
Sensible heat in dry flue gas
ni = molar or volumetric flowrate of flue gas component, i…. (CO2, N2, O2, SOx , NOx)
Heat in moisture (vapour)
Potential heat in due to the presence of combustibles in flue gas

## Slide 27
Vapor only

## Slide 28: ENERGY BALANCE TABLE
Reference : All gases at 25oC & 1 atm
Combustion Efficiency
Table B8
 | kJ/mol |  |  |  | 
TEMP | O2 | N2 | CO | CO2 | H2O
300 | 8.47 | 8.12 | 8.17 | 11.58 | 9.57

## Slide 29: ENERGY BALANCE TABLE
Reference : All gases at 25oC & 1 atm
Thermal Efficiency
Table B8
 | kJ/mol |  |  |  | 
TEMP | O2 | N2 | CO | CO2 | H2O
300 | 8.47 | 8.12 | 8.17 | 11.58 | 9.57
th

## Slide 30
Example 7 (Repeat Example 6)
Methane is completely burned with 10% excess air in a boiler to generate saturated steam. 90 % of the methane burns to form CO2 and the remaining 10% to form CO. both air and methane enter the boiler at 25oC and the combustion products leaving the boiler is at 300oC. Heat losses due to radiation, convection and from other uncounted sources is assumed to be approximately 5% of the total heat input
On the basis of 1 kmol/h of the methane and the lower fuel heating value,
develop a sankey diagram showing the percentage of useful heat and heat losses from various sources with respect to the net calorific value of the fuel.
estimate the flow rate (kg/hr) of steam produced, if the water enters the boiler at 25oC and leaves as saturated vapor at 1 atm.

## Slide 31
PFD and summary of Mass Balance
Methane
1000 mol/hr
Air
10 % excess air
10476 mol/hr
mol/hr CO2
mol/hr CO
mol/hr H2O
mol/hr O2
mol/hr N2
25 oC
25 oC
300 oC
900
100
2000
250
8276
H2O (l), 25oC
mw kg/h
H2O (saturated vapor), 1 atm

## Slide 32: ENERGY BALANCE TABLE
Reference : All gases at 25oC & 1 atm
Table B8
 | kJ/mol |  |  |  | 
TEMP | O2 | N2 | CO | CO2 | H2O
300 | 8.47 | 8.12 | 8.17 | 11.58 | 9.57
Thermal Efficiency

## Slide 33: ENERGY BALANCE TABLE
Reference : All gases at 25oC & 1 atm
Table B8
 | kJ/mol |  |  |  | 
TEMP | O2 | N2 | CO | CO2 | H2O
300 | 8.47 | 8.12 | 8.17 | 11.58 | 9.57
Thermal Efficiency

## Slide 34
Useful heat (Quseful) is the net available heat for steam production

## Slide 35
Example 8
Methane is burned with air in an atmospheric gas boiler where saturated steam is produced at 1 atm. The methane enters the boiler at a rate of 10 m3/hr (STP) and 25oC and the water enters the boiler at 25oC. The methane is assumed to be completely burned in X % excess air to form CO2 and H2O. The flue gas leaving the boiler is at Tg oC. Heat losses due to radiation, convection and from other uncounted sources is assumed to be approximately 5% of the total heat input.
Sketch a process flow diagram of the above process
Based on the lower heating value, construct a sankey diagram showing the percentage of heat available and losses from various sources.
Calculate the combustion and thermal efficiencies of the above process
Estimate the flow rate (kg/hr) of steam produced.
Excess air (%) | Air temp (oC) | Flue gas temp (Tg oC)
10 | 25 | 300
50 | 25 | 300
10 | 25 | 200
10 | 200 | 300

## Slide 36: Boiler Analysis
Excess air (%) | Air temp (oC) | Flue gas temp (oC) | Thermal eff. (%) | Steam produced (kg/hr)
10 | 25 | 300 | 82.75 | 115.0
50 | 25 | 300 | 78.92 | 109.8
10 | 25 | 200 | 87.27 | 121.5
10 | 200 | 300 | 83.25 | 124.1
(i)
(ii)
(iii)
(iv)
Compare and draw conclusions on the effect of the following boiler operating parameters on the thermal efficiency and steam production
excess air (i & ii)
flue gas temperature (i & iii)
air temperature (i & iv)
Which operating parameter has the most significant effect?

## Slide 37
Methane
10 m3/hr (STP)
446 mol/hr)
Air
10 % excess air
4672.4 mol/hr
mol/hr CO2
mol/hr H2O
mol/hr O2
mol/hr N2
H2O (l), 25oC
m kg/h
H2O (v), 1 atm
25oC
Tg oC
Example 8 – Process Flow Diagram (PFD)
CH4 | + | 2 | O2 |  | CO2 + | 2 | H20
446
892
89.2
3691.2
??
??
??
??
??
??
Tair oC
??

## Slide 38
Useful heat (Quseful) is the net available heat for steam production

## Slide 39
Example 7 – Summary of Mass and Heat Balance
Reference temp. (25oC) ; CO2, CO, N2, O2, H2O ( gases)

## Slide 40
Example 8
Repeat example 7 to estimate the combustion and thermal efficiencies and also the flow rate (kg/hr) of steam if the combustion excess air is 50%.
Reference temp. (25oC) ; CO2, CO, N2, O2, H2O ( gases)
Qsteam = mw (hs – hf)
282405 = mw (2676 – 104.8)
mw ~ 109.8 kg/hr

## Slide 41
Example 9
Repeat example 7 to estimate the thermal efficiency and the flow rate (kg/hr) of steam if the flue gas leaving the boiler is further reduced to 200oC.
Reference temp. (25oC) ; CO2, CO, N2, O2, H2O ( gases)
Qsteam = mw (hs – hf)
312303 = mw (2676 – 104.8)
mw ~ 121.5 kg/hr

## Slide 42
Example 10
Repeat example 7 to estimate the thermal efficiency and the flow rate (kg/hr) of steam if the combustion air is preheated to 200oC.
Reference temp. (25oC) ; CO2, CO, N2, O2, H2O ( gases)

## Slide 43: Boiler Analysis
Excess air (%) | Air temp (oC) | Flue gas temp (oC) | Thermal eff. (%) | Steam produced (kg/hr)
10 | 25 | 300 | 82.75 | 115.0
50 | 25 | 300 | 78.92 | 109.8
10 | 25 | 200 | 87.27 | 121.5
10 | 200 | 300 | 83.25 | 124.1

## Slide 44
Example 11
Repeat example 7 to solve questions (b) and (c) on the basis of higher heating value.
Reference temp.n( 25oC) ; CO2, CO, N2, O2 (gas) ; H2O (l)

## Slide 45
Example 9 (Do by your own)
Steam boiler power plant in a petroleum refinery has an overall thermal efficiency on net calorific value of 85% and an output of 100,000 kg steam per hour. The steam is produced at a pressure of 20 bar and is superheated to 250oC from feed water at 25oC. The volumetric composition of hydrocarbon gas mixture that is used to fire the boiler is as follows; H2=24%, CH4=17%, C2H6=17% and C3H8= 42%. Assuming the fuel and 10% excess air are fed into the boiler at 25oC and undergo complete reaction (main combustion products are CO2 and H2O). The temperature (oC) of the flue gas leaving the boiler is 200oC.
Estimate the volumetric flowrate (Standard Cubic Meter per Hour (SCMH)) of hydrocarbon gas mixture. (5689.4 SCMH)
Estimate the percentage of uncounted heat losses (radiation, convection etc) from the boiler (7.45%)

## Slide 46
H/C mixture
? kmol/h
? m3/hr (STP)
Air (10% Excess)
? kmol/h
? mol% CO2
? mol% H2O
? Mol% O2
? mol% N2
H2O (l), 25oC C
100,000 kg/h
(hf=104.8 kJ/kg)
H2O (v), 20 bar, 250oC
(hg=2902 kJ/kg)
25oC
25oC
200 oC
Process Flow Diagram

## Slide 47
LHV = | 1295638 |  | kJ/kmol |  |  |  | 
Qs = | 279720000 |  | kJ/h | [100000 x (2902-104.8)] |  |  | 
Qf = | 329082353 |  | kJ/h | (Qs/0.85) |  |  | 
nf = | 254 |  | kmol/h | [Qf/LHVmixt ] |  |  | 
Vf= | 5689.4 |  | SCMH | [22.4 x nf] |  |  | 
the volumetric flowrate (SCMH) of hydrocarbon gas mixture required.
 | Y %mol | LHV (kJ/kmol) | LHVmixt (kJ/kmol)
CH4 | 17 | 802340 | 1295638
C2H6 | 17 | 1427870 | 
C3H8 | 42 | 2043960 | 
H2 | 24 | 241830 | 

## Slide 48
H/C mixture
254 kmol/hr
Air
4197.7 kmol/hr
449.6 kmol/hr CO2
703.6 kmol/hr H 2O
3316.2 kmol/hr N2
80.14 kmol/hr O2
H2O (l), 25oC (hf=104.8 kJ/kg)
100,000 kg/h
H2O (v), 20 bar, 250 oC, (hg=2902 kJ/kg)
25oC
25oC
200 oC
the percentage of uncounted heat losses (radiation, convection etc) from the boiler
Summary of mass balance

## Slide 51: Adiabatic Flame Temperature Calculation
If nf moles of fuel is completely burned under adiabatic condition, the energy balance equation becomes
Where…. Tad is the product temperature, which by definition is the adiabatic or theoretical flame temperature

## Slide 52
Example 10
Waste gas from a refinery containing mainly carbon monoxide is burned with 120 % excess air in a reactor. Both the fuel and air are fed at 25oC. The engineer designing the reactor must calculate the highest temperature that the reactor walls will have to withstand so that an appropriate material of construction can be chosen. On the basis of 1 mol of carbon monoxide, estimate the flame temperature assuming complete combustion.

## Slide 53
CO
1 mol
Air
X = 120% (2.2)
5.238 mol
1 mol CO2
4.138 mol N2
0.6 mol O2
25oC
25oC
Tad oC
Summary of mass balance
Basis : 1 mol CO
CO + ½O2  CO2

## Slide 54
Reference : all gases at 25oC

## Slide 55
Reference : all gases at 25oC

## Slide 56
Reference : all gases at 25oC
Trial & Error + Interpolation
(= 261.6-282.99)
(= 284.3-282.99)

## Slide 57
Reference : all gases at 25oC
USING MICROSOFT EXCEL : DATA  WHAT IF ANALYSIS  GOAL SEEK
Goal seeking
Total output – Total input = 0
Target value