## Slide 1: Thermodynamics II Chapter 3 Compressors
Mohsin Mohd Sies
Fakulti Kejuruteraan Mekanikal, Universiti Teknologi Malaysia

## Slide 2: Coverage
Introduction
Indicated Work, Mechanical Efficiency
Condition for Minimum Work
Isothermal Efficiency
Compressors with Clearance
Volumetric Efficiency, Free Air Delivery
Multistage Compression
Ideal Intermediate Pressure

## Slide 3: Introduction
Compressed air is air kept under a pressure that is greater than atmospheric pressure.
In industry, compressed air is so widely used that it is often regarded as the fourth utility, after electricity, natural gas and water.

## Slide 4
Compressed air is used for many purposes, including:
Pneumatics, the use of pressurized gases to do work
  Pneumatic post, using capsules to move paper and small goods through tubes.
  Air tools
  HVAC control systems
Vehicle propulsion (compressed air vehicle)
Energy storage (compressed air energy storage)
Air brakes, including:
  railway braking systems
  road vehicle braking systems
Scuba diving, for breathing and to inflate buoyancy devices
Refrigeration using a vortex tube
Gas dusters for cleaning electronic components that cannot be cleaned with water
Air-start systems in engines
Ammunition propulsion in:
  Air guns, Airsoft equipment, Paintball equipment
Usages

## Slide 5: Compressor types
Positive Displacement Machines (high pressure ratio, low mass flow rates)
  Rotating
    Screw compressors (Lysholm)
    Scroll compressor
    Roots blowers
  Alternating (Reciprocating Compressor)
Turbocompressors (low pressure ratio, high mass flow rates)
  Centrifugal compressor
  Axial compressor
  Mixed-flow compressor

## Slide 7
Reciprocating Compressor
Single Acting

## Slide 8
Reciprocating Compressor
Double Acting

## Slide 9
Piston-cylinder terminologies
TDC – Top Dead Center
BDC – Bottom Dead Center

## Slide 10
b – Bore, Diameter
s – Stroke
l – Connecting Rod Length
a – Crank Throw = ½ stroke
Piston-cylinder terminologies

## Slide 12: Compressor Operation
Process d – a : Intake or Induction
  Piston moves from TDC to BDC
  Intake valve opens and air induced into cylinder
  Pressure P1 and temperature T1 remain constant.
Process a – b : Compression
  Intake valve closes and piston moves towards TDC
  Compression follows the polytropic process Pvn=c until P2 is reached.

## Slide 13: Compressor Operation
Process b – c : Delivery
  Delivery valve opens
  Compressed air exits and delivered.
  Pressure P2 and temperature T2 remain constant.
Process c – d : Expansion
  Both valves remain closed as the cycle returns to the initial state
  Constant volume if without clearance
  Polytropic expansion if with clearance

## Slide 14: Indicated Work - Indicated by P-v diagram, (P-v diagram = Indicator diagram)
For a cycle
Recall polytropic relationship between two states

## Slide 15: Indicated Work
Can also be considered as open system
And since PV = mRT

## Slide 16: Power (and Rates)
Has to take into account single or double acting
Wind is work per cycle of P-v diagram.
If single acting, one cycle per crank revolution
If double acting, two cycles per crank revolution (one cycle each for both sides of piston face).
  Mass flow rate is doubled accordingly.

## Slide 17: Mechanical Efficiency
The actual power input into the compressor is larger than the indicated power, to overcome friction and other losses. Shaft power = Indicated power + Friction power loss
Other losses can also be taken into account accordingly

## Slide 18: Condition for Minimum Work
We aim to reduce the input work
d-a is the stroke, determined by cylinder design and measurement
P2 is desired delivery pressure. As long as P2 is reached, the compressor has done its job.
Only the compression process can be adjusted by varying n, the polytropic index.
Isothermal process (n=1) results in minimum work (smallest area).
Compressors are cooled by water jackets or cooling fins

## Slide 19: Isothermal Work, Isothermal Efficiency
Integrating by isothermal process, Pv=c
Isothermal efficiency

## Slide 20: Compressors with Clearance
Clearance is needed for free movements of piston and valves
Clearance volume is Vc.
When delivery is completed (b-c), there is still compressed air at P2 and T2 in the clearance volume.
When intake stroke begins at Vc, no outside air can enter yet until the residual compressed air has expanded down to P1 and T1.
Thus, having clearance reduces the volume of inducted air from (Va-Vc) originally to only (Va-Vd)

## Slide 21: Compressors with Clearance
Mass of air, ma = mb, and md = mc
The amount of air handled, m = ma – md = mb – mc
Wind = area abcd = area abef – area cefd
Even though Work depends on clearance, but work per unit mass does not depend on it.

## Slide 22: Free Air Delivery, FAD
FAD is the amount of air handled (delivered) by the compressor.
FAD is given as the volumetric flow rate of air (measured at free air conditions Po and To)
Actually, this is easier given by the mass flow rate since it does not depend on P and T

## Slide 23: Volumetric Efficiency
The mass of gas entering
The mass of gas that should fill the swept volume at the same reference condition (free air condition)
The volume of gas entering measured at free air condition
The swept volume of cylinder

## Slide 24: Volumetric Efficiency
The result above is assuming that the in-cylinder condition (T1, P1) is the same as free air condition (To, Po)

## Slide 25: Volumetric Efficiency
The entering air is actually being heated by the hot cylinder walls and there has to be a pressure difference (Po – P1) so that air can flow into the cylinder.
We can use the unchanging mass to get the correction factor to account for these differences

## Slide 26: Multistage Compression
For a given Vs, increasing rp will
  decrease ηv.
  Increase delivery temperature
To achieve high pressures while avoiding those problems
  Do Multistage Compression
At some intermediate pressure Pi, the gas is sent to a smaller cylinder to be compressed further.
This also allows us to cool the gas (intercooling) to reduce compression work.

## Slide 27: Multistage Compression

## Slide 28: Multistage Compression
Complete Intercooling if
  Intermediate temperature Ti is cooled back to the same temperature as T1.

## Slide 29: Optimum Intermediate Pressure
The chosen Pi affects the amount of compression work that has to be supplied.
An optimum Pi will give us the minimum compressor work.
Let’s assume complete intercooling.
Wtotal = WLow Stage + WHigh Stage
Since Ti = T1 ,

## Slide 30: Optimum Intermediate Pressure
For a fixed P1, T1 and P2, we can the optimum Pi that gives us minimum Wtotal by

## Slide 31: Optimum Intermediate Pressure
So, for minimum compressor work
  Complete intercooling
  Same pressure ratio for all stages
This can be generalized to more than two stages

## Slide 32: Optimum Intermediate Pressure
This can be generalized to more than two stages (z = number of stages, P1 = intake pressure, P2 = final pressure)
For minimum compressor work
  Complete intercooling
  Same pressure ratio for all stages